## Sheet1
Start/Offset | Size | Name | Type | R/W | Description
1 | 2 | SID | uint32 | R | A well-known value 0x53756e53, uniquely identifies this as a SunSpec Modbus Map
3 | 1 | ID | uint16 | R | A well-known value 1, uniquely identifies this as a SunSpec Common Model
4 | 1 | L | uint16 | R | Well-known # of 16-bit registers to follow: 66
5 | 16 | Manufacturer | string | R | A well-known value registered with SunSpec for
compliance: Ampt
21 | 16 | Model | string | R | Manufacturer specific value Communication Unit
37 | 8 | Reserved | - | -
45 | 8 | Version | string | R | Software Version
53 | 16 | Serial Number | string | R | Manufacturer specific value
69 | 1 | Device Address | int16 | R/W | Modbus Device ID
71 | 1 | ID | uint16 | R | Ampt SunSpec Vendor Code 64050
72 | 1 | L | uint16 | R | Variable number of 16-bit registers to follow: 12 + N*16
73 | 1 | DCA_SF | int16 | R | Current scale factor
74 | 1 | DCV_SF | int16 | R | Voltage scale factor
75 | 1 | Reserved | - | -
76 | 1 | DCkWh_SF | int16 | R | Energy Scale Factor
77 | 1 | Reserved | - | -
78 | 1 | N | uint16 | R | Number of strings
79 | 6 | Reserved | - | -
Ampt Gen3CU
Offset | Size | Name | Type | R/W | Description
95 | 2 | In2DCV | uint32 | R | String input 2 voltage in mV
97 | 2 | DCWh | uint32 | R | Daily integrated string output energy in Wh
99 | 1 | In1DCA | int16 | R | String input 1 current in mA
100 | 1 | In2DCA | int16 | R | String input 2 current in mA
Ampt Gen3CU
Offset | Size | Name | Type | R/W | Description
141 | 2 | In1DCV | uint32 | R | String input 1 voltage in mV
143 | 2 | In2DCV | uint32 | R | String input 2 voltage in mV
145 | 2 | DCWh | uint32 | R | Daily integrated string output energy in Wh
147 | 1 | In1DCA | int16 | R | String input 1 current in mA
148 | 1 | In2DCA | int16 | R | String input 2 current in mA